Electrical - IP56 rated combination switch and 4-pin plug socket for 3-phase, 415 volts, 50Hz at 20 amp rating (eg Clipsal 56 series).  GPO’s at 32 amp are acceptable, as all Coogee Chemicals prime movers are equipped with 32-10 amp adaptors. 

Either HRC fuses or circuit breakers rated for direct on-line starting for a 4kW induction motor;

[image: image1.png]ALTERNATE BULK STORAGE INSTALLATION

STORAGE TANK

sz

=

SO YOROIE
StR Q

15, POLCE
FiEBRGAE.

COOGEE
CHEMICALS.

T Ty




7.1 Typical Bulk Installation Layout 

1 - Stainless steel male Camlock coupling on delivery point (NATO 50/80mm)

2 - Chemflex T951 flexible 50/80mm NATO transfer hose.

3 - Clipsal 56 Series (or equiv) 3 phase 415 volt 4 pin general power outlet – 3-8 metres from delivery point.

4 - Product pump is generally trailer/tanker mounted.

5 - Safety shower/eye-wash facility located 5-10 metres from delivery point with unobstructed access.

6 - Potable/non-potable wash water hose within easy reach from delivery point.

[image: image2.png]TYPICAL BULK STORAGE INSTALLATION

STORAGE TANK ?

3
@0
comnosive
s

COOGEE
CHEMICALS
TRANSPORT

— Ao R 0L | CODGEE [REMEALS PTY
ittt 00, POLICE R | 1o Entrsecy
FIRE BRIGADE _|ResPuNSE 1800 000 655

s r ‘ W (I D)





Alternate Bulk Installation Layout 
This type of layout does not require product to be drained out of the delivery pipe-work and into a receptacle at the completion of the transfer. Quite simply, the product remaining in the hose is drained back into the road tanker so the transfer hose can be disconnected without spilling/losing any product to the bund.  

This requires a small two-three step platform with handrails for the driver to access the connection point at chest-height (1,800-1,900mm above the ground), and the pipe-work to be governed by an 80mm butterfly valve and Camlock connection with a sealed cap.

SULPHURIC ACID SOLUTION





SULPHURIC ACID SOLUTION





2P





UN1830








